Generator Interconnection Data Sheet

For Wholesale Generators Connected

to the PG&E Electric System

“at Voltages 60 kV and Above”

for the

P4 Retrofit Project

A Project of Davis Hydro

Generator Interconnection Data Sheet

Note: Generators who are submitting a Completed Application pursuant to PG&E’s Transmission Owners Tariff must completely fill out this Generator Interconnection Data Sheet as an integral part of their application.

1.	General Project Information

A.

Project Name

Street Address

City, State

Zip Code

Phone Number

Fax Number

Email Address

___Pit 4  Retrofit Project___

___Shasta-Trinity National Forest____

________Near Burney California

____________________________

___NA__________________

___NA__________________

___NA_______________

B.

Developer Name

Street Address

City, State

Zip Code

Phone Number

Fax Number

Email Address

___ Davis Hydro, LLC

___27264 Meadowbrook Drive________

___Davis CA                                    ____

___95616_________________________

___530 753-0562  __________________

___530 753 4707 _________________

___hydro@davis.com ______________

C.

Site Owner Name

Street Address

City, State

Zip Code

Phone Number

Fax Number

Email Address

___US Forest Service and PG&E

___Shasta-Trinity National Forest ______

2400 Washington Avenue, Redding, CA 96001
 (530) 242-2360 (front desk)

530-244-2978 (switchboard)

___ _____

_________________________________

_________________________________

D.	The anticipated operation date:          6/10/06

2.	Type of Project (select one)

| Cogeneration | ______ | Reciprocating. Engine | ______ |
| --- | --- | --- | --- |
| Biomass | ______ | Steam Turbine | ______ |
| Gas Turbine | ______ | Wind | ______ |
| Hydro | ___X__ |

Other

| Describe:_____________ | ______ |
| --- | --- |
| Photovoltaic | ______ |

3.	Maximum generator power delivered to PG&E grid at Point of Interconnection

| Generator rated output | + __750___ | kW |
| --- | --- | --- |
| Less generator auxiliary load: | Nil (other than exciter) | kW |
| Maximum net power delivered to PG&E Grid: | = __750___ | kW |
| Standby load to be served when generator is OFF: | ___1 kW__ | kW |

4.		Generator Information    (TBD means to be determined, following PG&E’s requirements or preference)

We expect to have one generator.  We will install multiple ground fault relaying on the generator side.  We will also have phase voltage and current imbalance detection on the secondary side of the transformer.

We oppose frequency metering as unnecessary and prone to nuisance trips in our experience.

| A. | Manufacturer | _______TBD_______________ |
| --- | --- | --- |
| B. | Year Manufactured | _______New___________ |
| C. | Rated Size: |

kW:

KVA:

Terminal Voltage

Power Factor (%):

~ 750

1 MVA if induction

__2400______

| 84 |
| --- |
|  | D. |

Type:

(select one)

Induction:

Synchronous:

D.C. with Inverter:

_X per PG&E

_X per PG&E

| ________ | No Preference – consult with PG&E. Most likely Synchronous |
| --- | --- |
| E. |

Synchronizing

Auto

Manual

Relay Supervision (y/n)

___X_____

________

| _Device 25 per PG&E request _______ |
| --- |
|  | F. | Voltage: |

Output

Interconnection

_2,400

kV

kV

G.

Phase:

(select one)

1(

3(

________

| ____3____ |
| --- |
|  | H. |

Connection (Where?)

(select one) (Generator/Transformer)

Delta

Grounded WYE

Ungrounded

Preferred

________

| ________ | or PG&E |
| --- | --- |
| I. |

Inertia Constant

(if known)

____________

| lb-ft( |
| --- |
|  | J. | Generator Voltage Regulation Range |

| _____________ |
| --- |
| K. | Generator Power Factor Regulation Range |

_____________

5.	Generating Grounding

If the generator output is greater than 40kW (individually or as an aggregate group), ground protection will be required.  If grounding will be required, please indicate type of ground detection below:

| a. Wye Grounded/Delta Ground Bank with Overcurrent Relay | _______ |
| --- | --- |
| b. Wye Grounded/Broken Delta: Ground Bank with Low Pick-up Overvoltage Relay | ___59N___ |
| c. Current Transformer with Overcurrent Relay: In Neutral of Dedicated Transformer | ___51G___ |
| d. Potential Transformer with Voltage Relay1: In Neutral of Dedicated Transformer | _______ |
| Other: | PG&E’s preference_ |

All above methods produce false tripping due to phase imbalances and jitter .  This site is on a long radial prone to noise and transients.  We will be pleased to work with PG&E engineers to minimize nuisance tripping.

We will expect to install both b and d and adjust the trip voltages based on field experience. However the transformers will be the same in both b & d.  We will follow PG&E guidance.  Usually sporadic phase voltage imbalance controls set points.

Note:  The size of these items are speculative related to the total amount of power that can be absorbed by the distribution system.

6.		Step-Up Transformer Data

| A. | Rated MVA | _> 0.75 | MVA |
| --- | --- | --- | --- |
| B. | Cooling Type | _____oil/ air__________ |
| C. | Impedance - Z | ___TBD__ | % Impedance |
| D. |

Primary Voltage

Secondary Voltages

12 kV

4160 /480

KW   1.75

| KW 1.75 |
| --- |
| E. | Available H.V. Taps |

_________

_________

_________

_________

_________

_________

kV

kV

kV

kV

kV

| kV | Available L.V. Taps |
| --- | --- |

_________

_________

_________

_________

_________

_________

kV

kV

kV

kV

kV

| kV |
| --- |
| F. | Please indicate present tap settings: |

H.V Tap: 12 KV/ Per PG&E

L.V Tap: 4160, 480 ( two transformers)

kV

| V |
| --- |
|  | G. | Does transformer have tap changing under load? | ___NO________ |
| H. |

Is transformer a regulating-type transformer?  NO

If yes, please indicate regulating voltage range and the number of steps.

_____________ kV to ______________ kV Number of steps _________

I.

Please indicate how the transformer windings are connected: TBD

What services are permitted and recommended.

We will follow PG&E recommendations.

H.V. Side:

____

____

____

Wye

Grounded Wye

| Delta | L.V. Side: |
| --- | --- |

____

____

____

Wye

Grounded Wye

| Delta |
| --- |
| J. | Transformer Fuse | Type: | __PGE_____ | Size | _PGE______ |
| K. | If the transformer test report is not available, please provide the following impedances using the MVA base given in (10.A) above: |

RT

XT

BT

GT

per unit resistance

per unit reactance

per unit magnetizing susceptance

per unit core loss conductance

_________

_________

_________

_________

pu

pu

pu

pu

L.

Other comments regarding the transformer?

We will follow PG&E’s requirements.  We expect that we will be using ungrounded delta generators.  This will suggest wye on the low side of the transformer.  We will follow PG&E recommendations.

| _________________________________________________________________________ |
| --- |
| M | Desired transformer connection: |
|  | Delta |

Grounded

Wye

Ungrounded

| Wye |
| --- |
| PG&E Side | ____X___ | ________ | ________ |
| Generator Side | ________ | ________ | ____X___ |

7.	Please provide two original prints and one reproducible copy (no larger than 36” x 24”) of the following:

SITE DRAWING to scale, showing generator location and point of interconnection with PG&E.

Please see Drawing P4-E-2

For generation greater than 1000 kW provide the following:

Substation grounding drawings showing all ground connections.

Please see Drawing P4-E-2 Insert.

A list of the amount and location of the shunt capacitor compensation that will be provided (induction generators only).

To be worked out with PG&E.

SINGLE LINE DIAGRAM, showing switches/disconnects of the proposed interconnection, including the required protection devices and breakers.

Please See Drawing P4-E-1

THREE LINE DIAGRAM, showing the proposed CTs and PTs as they are connected to the relays and meters.

Please See Drawing P4-E-3

DESCRIPTION of operation and elementary drawings, showing the synchronization (if appropriate), and tripping of breakers by the required relays.  (If not provided, they may be requested after approval of the single and three line diagrams.)

LIST of relays, switches and revenue meters (if customer provided), disconnects, etc., specified to meet the requirements of PG&E’s Interconnection Handbook and include the following information:.

Manufacturer’s name and model number, with each device listed.

Range of available settings.

Proposed settings.

Ratio of associated current and potential transformers.  If multi-ratio, state the available ratios and which one is proposed.

We will supply all requested information.  Currently we are requesting advice on the following:

We will request 12 kV service with 12 kV metering.

We probably will use two transformers 12,000/4160/2,400 and 12,000/480/277

We assume PG&E will supply:

Hi side Current Limiting fusing by PG&E

Hi side Fused Disconnects.

Primary metering CTs and VTs for primary metering.

High side ground fault and line balance detection.

Air switch(es)

Advice and review of Capacitors

Reclosure discussion

8.		Proposed breaker(s) will be equipped with:

| Undervoltage Release | X____ |
| --- | --- |
| D.C. Trip | X_____ |

9.	The following information is required for Induction Generators only.

Do you wish reclose blocking?  Most likely To be discussed.

Note:  we test automatically.  Sufficient capacitance may be on the line now, or in the future, and your generator may self-excite unexpectedly.

Ok.  We will Look at it with your engineers and add PFCs as appropriate.

We will work with PG&E to install whatever PFCs required for stable operation.  Normally we recommend PFCs to bring PF at transformer primary to about .95.  Each induction generator will have parallel PFC’s to match.  However we have not had experience with such long high capacitance distribution system radials, and will work with PG&E for a stable system.

Information contained in Sections 10 through 15 is required only for Synchronous Generators.  It is acceptable to provide IEEE block diagrams for the dynamic data specified in Sections 10 through 15.

15.	Turbine-Governor Information

Please complete Part A for steam, gas or combined-cycle turbines, Part B for hydro turbines, and Part C for both.

B.	Hydro turbines: (these have not been specified so the following is our expectations)

| 1.) | What is the turbine efficiency at rated load? Typical | ____82____ | % |
| --- | --- | --- | --- |
| 2.) | What is the length of the penstock? ( longer) | 160______ | ft |
| 3.) |

What is the average cross-sectional area of the penstock.

| We expect one penstock about 54” in diameter. | _________ | ft2 |
| --- | --- | --- |
| 4.) | What is the typical maximum head (vertical distance from the bottom of the penstock, at the gate, to the water level)? |

__55____

| ft |
| --- |
| 5.) | Is the water supply run-of-the-river or reservoir? | __RR______ |
|  | 6.) | What is the water flow rate at the typical maximum head? ( design head is 49’. ) | __350____ | ft3/sec |
| 7.) | What is the average energy rate? | ___________ | kW-hrs/acre-ft |
| 8.) | What is the estimated yearly energy production? | 8 GWH__ |

C.	Complete this section for each machine, independent of the turbine type.

| 1.) | Turbine manufacturer | ___T. B. D. _____ |
| --- | --- | --- |
|  | 2.) | Maximum turbine power output (Shaft) | _ 0.8___(shaft)______ | MW |
| 3.) | Minimum turbine power output (while on line ) | __.75__(wire)_ | MW |
| 4.) | Governor information: | None |
| a: Droop setting (speed regulation) | _None __________ |
| b: Is the governor mechanical-hydraulic or electro-hydraulic? (Electro-hydraulic governors have an electronic speed sensor and transducer.) |

Mechanical

_________________

c:	Please provide below any time constants you have from the manufacturer describing the speed response of the governor.  Be sure to identify each time constant.

______________________________________________

______________________________________________

______________________________________________

No Governor

_________________

_________________

_________________

sec

sec

sec

d:	Other comments regarding the turbine governor system?

______________________________________________

______________________________________________

______________________________________________

______________________________________________

Completed By:  	Richard D. Ely ,          Date:  	____5/18/04____________________________

Phone Number:	__530 753-8864  Fax Number:	_530 – 753-4707  E-Mail address:	 Hydro@davis.com

# Footnotes

This is PG&E’s preferred ground detection.

Capacitor Trip is not acceptable.